## Blank
[15 empty] | P204 | Reset Drive Params | 5 | 1 | P900 | Soft PLC Status
[6 empty] | Manual SP (eng units): | [8 empty] | P204 | Reset SoftPLC Params | 11 | 2 | P901 | Soft PLC Command | 0
SP Source: | [5 empty] | P918 | [8 empty] | P015 | AO2 Value |  | 3 | P902 | Scan Time
P920 | [14 empty] | P100 | Accel |  | 4 | P903 | Select User or PID | 1
Current SP (eng units): | [11 empty] | SoftPLC CTRL |  |  | P101 | Decel |  | 5 | P904 | Action: SoftPLC not running | 0
P911 | [11 empty] | P900 | r.o. | PID Status (ro) | P133 | Min CO (hz) |  | 6 | P910 | PID App Version
SP Filter: | [11 empty] | P903 |  | Use PID Application | P134 | Max CO (hz) |  | 7 | P911 | SP | 0
P935 | 0 | [7 empty] | P917 |  |  | P901 |  | PID ENABLE | P135 | Current Limit | 6.3 | 8 | P912 | SP1 | n.a.
[15 empty] | P136 | Man Torque Boost | n.a. | 9 | P913 | SP2 | n.a.
[15 empty] | P137 | Auto Torque Boost | n.a. | 10 | P914 | SP3 | n.a.
[6 empty] | P929 | 2 |  |  |  |  | Assumptions (see Hardware Video): |  |  | P220 | LOC/REM Sel Source |  | 11 | P915 | SP3 | n.a.
Bumpless Mode: |  |  | P931 (P) | 1 | [7 empty] | Mode: | Always LOCAL |  | P221 | LOC Ref Sel |  | 12 | P916 | PV
P930 |  |  | P932 (I) | 5 |  |  |  | PV Source (AI1): |  |  |  | Run/Stop | DI1 |  | P222 | REMO Ref Sel | n.a. | 13 | P917 | CO
|  |  | P933 (D) | 0 |  | Current PV (ro) |  | P921 |  |  |  | Man/Auto | DI2 |  | P223 | LOC Fwd/Rev Sel | n.a. | 14 | P918 | SP for Manual Mode | 0
|  |  | P934 (t) | 0.1 |  | P916 | r.o. |  |  |  |  | PV | AI1 (4-20mA)/AO1(0-10V) |  | P224 | LOC Run/Stop Sel |  | 15 | P919 | PID Controller Status
[12 empty] | SP | HMI |  | P231 | AI1 Funct |  | 16 | P920 | SP Source
Motor: | [11 empty] | Action | Direct (Forward) Acting |  | P232 | AI1 Gain |  | 17 | P921 | PV Source
P100 |  | Acceleration (s) |  |  |  |  | Fwd/Rev Acting: | P928 |  |  |  |  | = Good to go! |  | P233 | AI1 Type |  | 18 | P922 | PV Min
P101 |  | Decel (S) | [10 empty] | = Needs a value |  | P234 | AI1 Offset |  | 19 | P923 | PV Max
P133 |  | Drive Freq Min |  |  |  | PV Conditioning (AI1): | [6 empty] | = Default Value |  | P235 | AI1 Filter |  | 20 | P924 | PV Low Alarm Level
P134 |  | Drive Freq Max |  |  |  | P231 |  | AI1 = PV |  |  |  | r.o. | = Read Only |  | P236 | AI2 Funct | n.a. | 21 | P925 | PV Low Alarm Time
P400 |  | Rated Voltage |  |  |  | P232 |  | AI1 Gain | [6 empty] | P237 | AI2 Gain | n.a. | 22 | P926 | PV High Alarm Level
P401 |  | Full Load Amps |  |  |  | P233 |  | AI1 Signal Type | [6 empty] | P238 | AI2 Type | n.a. | 23 | P927 | PV High Alarm Time
P402 |  | Rated Speed (rpm) |  |  |  | P234 |  | AI1 Offset (%) | [6 empty] | P239 | AI2 Offset | n.a. | 24 | P928 | Forward or Reverse acting
P404 |  | Rated Power (1 hp) |  |  |  | P235 |  | AI1 Filter (Sec) | [6 empty] | P240 | AI2 Filter | n.a. | 25 | P929 | Auto/Man Select | 2
[15 empty] | P263 | DI1 Funct |  | 26 | P930 | Bumpless Mode
Drive Control: | [5 empty] | P922 |  | PV Min. (@ CO = 0%) | [6 empty] | P264 | DI2 Funct |  | 27 | P931 | P | 1
P220 |  | Always LOCAL |  |  |  | P923 |  | PV Max. (@ CO = 100%) | [6 empty] | P265 | DI3 Funct | n.a. | 28 | P932 | I | 5
P221 |  | Spd ref ctrl (SoftPLC) | [12 empty] | P266 | DI4 Funct | n.a. | 29 | P933 | D | 0
P224 |  | Run Stop via Dix |  | Display: | [10 empty] | P400 | Rated Voltage | 0 | 30 | P934 | Sample Time | 0.1
P263 |  | DI1 = Run Stop |  | P510 |  | Units for all SoftPLC params | [8 empty] | P401 | Full Load Amps | 0 | 31 | P935 | PV Filter | 0.15
P264 |  | DI2 controls Man/Auto |  | P511 |  | Decimal Pt for all SofPLC Params | [8 empty] | P402 | Rated Speed | 0 | 32 | P936 | Sleep Mode - Wake Value | n.a.
[15 empty] | P404 | Rated Power | 0 | 33 | P937 | Sleep Mode - Wake Time | n.a.
[15 empty] | P510 | Soft PLC Eng Unit |  | 34 | P938 | Sleep Mode - Sleep Value | n.a.
[15 empty] | P511 | SoftPLC Dec Point |  | 35 | P939 | Sleep Mode - Sleep Time | n.a.
STUFF NOT USED IN OUR DEMO
Alarms: |  |  |  | SP Config Options | [5 empty] | Sleep Mode
P275 | 46 | DO1 = Alarm Low Level (A760, F761) |  | P236 | 16 | AI2 = SP, If using AI for SP (we arne't) |  |  |  | P936 |  | Wakeup Deviation
P278 | 47 | DO2 = Alarm High Level (A762/F763) |  | P265 |  | DI3 = Multi SP |  |  |  | P937 |  | Time to wakeup
|  |  |  | P266 |  | DI4 = Multi SP |  |  |  | P938 |  | Motor speed to activate Sleep
Motor: |  |  |  | P912 |  | SP 1 for Multi SP |  |  |  | P939 |  | Time to activate Sleep
P136 | 5 | Manual Torque Boost (V/f) |  | P913 |  | SP 2 for Multi SP
P137 | 0 | Manual Torque Boost (V/f) |  | P914 |  | SP 3 for Multi SP |  |  |  | P208 |  | Full Scale Speed Reference, see P210 for decimal point
|  |  |  | P915 |  | SP 4 for Multi SP |  |  |  | P210 | 1 | Speed Ref Decimal Point
[10 empty] | P209 | 3 | Eng Units of Speed Ref
SP
PV
+
-
PID
Man SP
MAN
AUTO
CO (%)
– – – – – – DISCLAIMER – – – – – – – THIS INFORMATION PROVIDED BY AUTOMATIONDIRECT.COM IS PROVIDED “AS IS” WITHOUT A GUARANTEE OF ANY KIND. We do not guarantee that it is suitable for your particular application, nor do we assume any responsibility for it’s use in your application. It is provided solely as an example and it is incumbent upon the user to determine the applicability of information/code, and to fully test it prior to use.
WEG PID Config. Tool
Note on AB1: 0 = no app 1 = Installing App 2 = Incompat App 3 = App Stopped 4 = App running
Note on AB2: 0 = Stop App 1 = Run App
Note on K3: MANUAL SETPOINT
Note on AB3: READ ONLY Scan Time in seconds
Note on C4: Setpoint Source 0 = HMI or Com Module (put value in P911) 1 = SP via AI1 2 = SP via AI2 3 = SP via E. Pot 4 = Two SP's via DI3 (P912, 913) 5 = Three SP's via DI3, DI4 (P192, 913, 914) 6 = Four SP's via DI3, DI4 (P912, 913, 914, 915)
Note on AB4: 0 = user app 1 = PID Controller
Note on AB5: 0 = Disabled 1 = Alarm (A708) 2 = Fault (F709)
Note on C6: Setpoint in Auto for HMI or coms (P920 = 0) in Eng Units. If P920 != 0, Show present SP
Note on AB6: READ ONLY
Note on Q7: Use built-in PID Application (not user ladder code)
Note on AB7: Setpoint in Auto for HMI or coms (P920 = 0) in Eng Units. If P920 != 0, Show present SP
Note on N8: CONTROl OUTPUT (%) (read only) Where: 0% = P133 (Min Speed) 100% = P134 (Max Speed)
Note on Q8: Set to a "1" to start application running
Note on AB8: Multi Point SP via Dix in Eng Units (P950 - 4, 5 or 6)
Note on AB9: Multi Point SP via Dix in Eng Units (P950 - 4, 5 or 6)
Note on AB10: Multi Point SP via Dix in Eng Units (P950 - 4, 5 or 6)
Note on K11: PID MODE: 0 Manual 1 Automatic 2 Man/Auto via DI2
Note on AB11: Multi Point SP via Dix in Eng Units (P950 - 4, 5 or 6)
Note on AB12: READ ONLY In units defined in P921 Scale defined by P922, 923 P916 = AI% x (P923-P922) + P922
Note on C13: Man->Auto Auto->Man 0 SP=SP SP=SP 1 SP=PV SP=SP (Bumpless) 2 SP=SP SP=PV 3 SP=PV SP=PV (Bumpless)
Note on H13: Folea, Rick: Integral Gain units: 1/Sec
Note on AB13: Controller Output in % Where 0% is P133 (motor min speed) and 100% is P134 (motor max speed)
Note on H14: Folea, Rick: Differential Gain units: Sec
Note on M14: PV Source: 1 = Analog Input AI1 2 = Analog Input AI2 3 = AI1-AI2
Note on AB14: Controller output in hz.
Note on H15: Folea, Rick: Sample Time (Sec)
Note on AB15: rfolea: bit0 - Sleep mode active = 1 (A750) bit1 - PID in manual Manual(0) or Automatic (1) bit2 - PV low level alarm = 1 (A760) bit3 - PV high level fault = 1 (F761) bit4 - PV high level alarm = 1 (A762) bit5 - PV high level fault = 1 (F763)
Note on AB16: 0 = HMI or Coms (P911) 1 = AI1 2 = AI2 3 = Elect Pot 4 = Two SP via DI3 (P912 and P913) 5 = Three SP via DI3, DI4 (P912, P913, P914) 6 = Four SP via DI3, DI4 (P912, P913, P914, P915)
Note on AB17: 1 = AI1 2 = AI2 3 = AI1 - AI2
Note on C18: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on M18: 1 = Direct Acting (Forward Acting) 2 = Reverese Acting
Note on AB18: Expected PV when CO is 0 In eng units defined in P510, 511
Note on C19: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on AB19: Expected PV when CO is 100% In eng units defined in P510, 511
Note on AB20: If PV falls below this value for longer than the time in P925 - generate an alarm In units defined by P510, P511
Note on K21: 0 = Speed Ref. 4 = PTC 7 = PLC User app 16 = SP 17 = PV
Note on AB21: How long condition should remain before alarming. In seconds
Note on AB22: If PV goes above this value for longer than the time in P927 - generate an alarm In units defined by P510, P511
Note on K23: 0 = 0 to 10V OR 0-20mA 1 = 4 to 20 mA 2 = 10 to 0V OR 20 to 0mA 3 = 20 to 4mA
Note on AB23: How long condition should remain before alarming. In seconds
Note on AB24: 0 = disable PID controller 1 = Forward (or Direct) mode 2 = Reverse Mode
Note on AB25: 0 = Manual 1 = Automatic 2 = via DI2 M(0), A(1)
Note on AB26: Man->Auto Auto->Man 0 SP=SP SP=SP 1 SP=PV SP=SP (bumplees) 2 SP=SP SP=PV 3 SP=PV SP=PV (Bumpless)
Note on K27: Expected PV at CO = 0%
Note on C28: 0 = Always Local 1 = Always Remote 4 = Dix 5 = Seiral/USB LOCAL 6 = Serial/USB REMOTE 11 = SoftPLC
Note on K28: Expected PV at CO = 100%
Note on C29: 0 = HMI 1 = AI1 2 = AI2 3 = Potentiometer 4 = FI 5 = AI1+AI@ >0 6 = AI1 + AI2 7 = Elect Pot 8 = MultiSpeed 9 = Seia USB 12 = SoftPLC 14 AI1>0 15 = AI2 >0 16 = Potentiometer >0 17 = FI >0
Note on C30: 0 = HMI Keys 1 = Dix 2 = Serial USB 5 = SoftPLC
Note on C31: 0 = not used 1 = Run Stop … lots more ...
Note on I31: Units to show on LCD For Soft PLC Params 2 = V 3 = Hz 5 = % 7 = rpm all others show nothing
Note on C32: 0 = not used 1 = Run Stop … lots more .. 50 = PID Man/Auto
Note on I32: Decimal Point for Soft PLC Params 0 = wxyz 1 = wxy.z 2 = wx.yz 3 = w.xyz
Note on P32: (for 100% make it same as P208)
Note on I40: 0 = Speed Ref. 4 = PTC 7 = PLC User app 16 = SP 17 = PV
Note on O45: Folea, Rick: Scale the display for the speed reference in paramter 2. We'll enter that as a 600 for 60 Hz (and adjust the formatting parameters accordingly (P209, 210)
Note on O46: Decimal Point 0 = wxyz 1 = wxy.z 2 = wx.yz 3 = w.xyz
Note on O47: 2 = V 3 = Hz 5 = % 7 = rpm all others show nothing

## As ued in video
[15 empty] | P204 | Reset Drive Params | 5 | 1 | P900 | Soft PLC Status
[6 empty] | Manual SP (eng units): | [8 empty] | P204 | Reset SoftPLC Params | 11 | 2 | P901 | Soft PLC Command | 0
SP Source: | [5 empty] | P918 | [8 empty] | P015 | AO2 Value |  | 3 | P902 | Scan Time
P920 | 0 | [13 empty] | P100 | Accel | 0.2 | 4 | P903 | Select User or PID | 1
Current SP (eng units): | [11 empty] | SoftPLC CTRL |  |  | P101 | Decel | 0.2 | 5 | P904 | Action: SoftPLC not running | 0
P911 | 6 | [10 empty] | P900 | r.o. | PID Status (ro) | P133 | Min CO (hz) | 25 | 6 | P910 | PID App Version
SP Filter: | [11 empty] | P903 |  | Use PID Application | P134 | Max CO (hz) | 50 | 7 | P911 | SP | 6
P935 | 0 | [7 empty] | P917 |  |  | P901 |  | PID ENABLE | P135 | Current Limit | 6.3 | 8 | P912 | SP1 | n.a.
[15 empty] | P136 | Man Torque Boost | n.a. | 9 | P913 | SP2 | n.a.
[15 empty] | P137 | Auto Torque Boost | n.a. | 10 | P914 | SP3 | n.a.
[6 empty] | P929 | 2 |  |  |  |  | Assumptions (see Hardware Video): |  |  | P220 | LOC/REM Sel Source | 0 | 11 | P915 | SP3 | n.a.
Bumpless Mode: |  |  | P931 (P) | 1 | [7 empty] | Mode: | Always LOCAL |  | P221 | LOC Ref Sel | 12 | 12 | P916 | PV
P930 | 0 |  | P932 (I) | 5 |  |  |  | PV Source (AI1): |  |  |  | Run/Stop | DI1 |  | P222 | REMO Ref Sel | n.a. | 13 | P917 | CO
|  |  | P933 (D) | 0 |  | Current PV (ro) |  | P921 | 1 |  |  | Man/Auto | DI2 |  | P223 | LOC Fwd/Rev Sel | n.a. | 14 | P918 | SP for Manual Mode | 0
|  |  | P934 (t) | 0.1 |  | P916 | r.o. |  |  |  |  | PV | AI1 (4-20mA)/AO1(0-10V) |  | P224 | LOC Run/Stop Sel | 1 | 15 | P919 | PID Controller Status
[12 empty] | SP | HMI |  | P231 | AI1 Funct | 17 | 16 | P920 | SP Source | 0
Motor: | [11 empty] | Action | Direct (Forward) Acting |  | P232 | AI1 Gain | 1 | 17 | P921 | PV Source | 1
P100 | 0.2 | Acceleration (s) |  |  |  |  | Fwd/Rev Acting: | P928 | 1 |  |  |  | = Good to go! |  | P233 | AI1 Type | 0 | 18 | P922 | PV Min | 1.46
P101 | 0.2 | Decel (S) | [10 empty] | = Needs a value |  | P234 | AI1 Offset | 0 | 19 | P923 | PV Max | 12.63
P133 | 25 | Drive Freq Min |  |  |  | PV Conditioning (AI1): | [6 empty] | = Default Value |  | P235 | AI1 Filter | 0.25 | 20 | P924 | PV Low Alarm Level | 0
P134 | 50 | Drive Freq Max |  |  |  | P231 | 17 | AI1 = PV |  |  |  | r.o. | = Read Only |  | P236 | AI2 Funct | n.a. | 21 | P925 | PV Low Alarm Time | 60
P400 | 220 | Rated Voltage |  |  |  | P232 | 1 | AI1 Gain | [6 empty] | P237 | AI2 Gain | n.a. | 22 | P926 | PV High Alarm Level | 20
P401 | 3.7 | Full Load Amps |  |  |  | P233 | 0 | AI1 Signal Type | [6 empty] | P238 | AI2 Type | n.a. | 23 | P927 | PV High Alarm Time | 60
P402 | 3450 | Rated Speed (rpm) |  |  |  | P234 | 0 | AI1 Offset (%) | [6 empty] | P239 | AI2 Offset | n.a. | 24 | P928 | Forward or Reverse acting | 1
P404 | 5 | Rated Power (1 hp) |  |  |  | P235 | 0.25 | AI1 Filter (Sec) | [6 empty] | P240 | AI2 Filter | n.a. | 25 | P929 | Auto/Man Select | 2
[15 empty] | P263 | DI1 Funct | 1 | 26 | P930 | Bumpless Mode | 0
Drive Control: | [5 empty] | P922 | 1.46 | PV Min. (@ CO = 0%) | [6 empty] | P264 | DI2 Funct | 50 | 27 | P931 | P | 1
P220 | 0 | Always LOCAL |  |  |  | P923 | 12.63 | PV Max. (@ CO = 100%) | [6 empty] | P265 | DI3 Funct | n.a. | 28 | P932 | I | 5
P221 | 12 | Spd ref ctrl (SoftPLC) | [12 empty] | P266 | DI4 Funct | n.a. | 29 | P933 | D | 0
P224 | 1 | Run Stop via Dix |  | Display: | [10 empty] | P400 | Rated Voltage | 220 | 30 | P934 | Sample Time | 0.1
P263 | 1 | DI1 = Run Stop |  | P510 | 0 | Units for all SoftPLC params | [8 empty] | P401 | Full Load Amps | 3.7 | 31 | P935 | PV Filter | 0.15
P264 | 50 | DI2 controls Man/Auto |  | P511 | 2 | Decimal Pt for all SofPLC Params | [8 empty] | P402 | Rated Speed | 3450 | 32 | P936 | Sleep Mode - Wake Value | n.a.
[15 empty] | P404 | Rated Power | 5 | 33 | P937 | Sleep Mode - Wake Time | n.a.
[15 empty] | P510 | Soft PLC Eng Unit | 0 | 34 | P938 | Sleep Mode - Sleep Value | n.a.
[15 empty] | P511 | SoftPLC Dec Point | 2 | 35 | P939 | Sleep Mode - Sleep Time | n.a.
STUFF NOT USED IN OUR DEMO
Alarms: |  |  |  | SP Config Options | [5 empty] | Sleep Mode
P275 | 46 | DO1 = Alarm Low Level (A760, F761) |  | P236 | 16 | AI2 = SP, If using AI for SP (we arne't) |  |  |  | P936 |  | Wakeup Deviation
P278 | 47 | DO2 = Alarm High Level (A762/F763) |  | P265 |  | DI3 = Multi SP |  |  |  | P937 |  | Time to wakeup
|  |  |  | P266 |  | DI4 = Multi SP |  |  |  | P938 |  | Motor speed to activate Sleep
Motor: |  |  |  | P912 |  | SP 1 for Multi SP |  |  |  | P939 |  | Time to activate Sleep
P136 | 5 | Manual Torque Boost (V/f) |  | P913 |  | SP 2 for Multi SP
P137 | 0 | Manual Torque Boost (V/f) |  | P914 |  | SP 3 for Multi SP |  |  |  | P208 |  | Full Scale Speed Reference, see P210 for decimal point
|  |  |  | P915 |  | SP 4 for Multi SP |  |  |  | P210 | 1 | Speed Ref Decimal Point
[10 empty] | P209 | 3 | Eng Units of Speed Ref
SP
PV
+
-
PID
Man SP
MAN
AUTO
CO (%)
– – – – – – DISCLAIMER – – – – – – – THIS INFORMATION PROVIDED BY AUTOMATIONDIRECT.COM IS PROVIDED “AS IS” WITHOUT A GUARANTEE OF ANY KIND. We do not guarantee that it is suitable for your particular application, nor do we assume any responsibility for it’s use in your application. It is provided solely as an example and it is incumbent upon the user to determine the applicability of information/code, and to fully test it prior to use.
WEG PID Config. Tool
Note on AB1: 0 = no app 1 = Installing App 2 = Incompat App 3 = App Stopped 4 = App running
Note on AB2: 0 = Stop App 1 = Run App
Note on K3: MANUAL SETPOINT
Note on AB3: READ ONLY Scan Time in seconds
Note on C4: Setpoint Source 0 = HMI or Com Module (put value in P911) 1 = SP via AI1 2 = SP via AI2 3 = SP via E. Pot 4 = Two SP's via DI3 (P912, 913) 5 = Three SP's via DI3, DI4 (P192, 913, 914) 6 = Four SP's via DI3, DI4 (P912, 913, 914, 915)
Note on AB4: 0 = user app 1 = PID Controller
Note on AB5: 0 = Disabled 1 = Alarm (A708) 2 = Fault (F709)
Note on C6: Setpoint in Auto for HMI or coms (P920 = 0) in Eng Units. If P920 != 0, Show present SP
Note on AB6: READ ONLY
Note on Q7: Use built-in PID Application (not user ladder code)
Note on AB7: Setpoint in Auto for HMI or coms (P920 = 0) in Eng Units. If P920 != 0, Show present SP
Note on N8: CONTROl OUTPUT (%) (read only) Where: 0% = P133 (Min Speed) 100% = P134 (Max Speed)
Note on Q8: Set to a "1" to start application running
Note on AB8: Multi Point SP via Dix in Eng Units (P950 - 4, 5 or 6)
Note on AB9: Multi Point SP via Dix in Eng Units (P950 - 4, 5 or 6)
Note on AB10: Multi Point SP via Dix in Eng Units (P950 - 4, 5 or 6)
Note on K11: PID MODE: 0 Manual 1 Automatic 2 Man/Auto via DI2
Note on AB11: Multi Point SP via Dix in Eng Units (P950 - 4, 5 or 6)
Note on AB12: READ ONLY In units defined in P921 Scale defined by P922, 923 P916 = AI% x (P923-P922) + P922
Note on C13: Man->Auto Auto->Man 0 SP=SP SP=SP 1 SP=PV SP=SP (Bumpless) 2 SP=SP SP=PV 3 SP=PV SP=PV (Bumpless)
Note on H13: Folea, Rick: Integral Gain units: 1/Sec
Note on AB13: Controller Output in % Where 0% is P133 (motor min speed) and 100% is P134 (motor max speed)
Note on H14: Folea, Rick: Differential Gain units: Sec
Note on M14: PV Source: 1 = Analog Input AI1 2 = Analog Input AI2 3 = AI1-AI2
Note on AB14: Controller output in hz.
Note on H15: Folea, Rick: Sample Time (Sec)
Note on AB15: rfolea: bit0 - Sleep mode active = 1 (A750) bit1 - PID in manual Manual(0) or Automatic (1) bit2 - PV low level alarm = 1 (A760) bit3 - PV high level fault = 1 (F761) bit4 - PV high level alarm = 1 (A762) bit5 - PV high level fault = 1 (F763)
Note on AB16: 0 = HMI or Coms (P911) 1 = AI1 2 = AI2 3 = Elect Pot 4 = Two SP via DI3 (P912 and P913) 5 = Three SP via DI3, DI4 (P912, P913, P914) 6 = Four SP via DI3, DI4 (P912, P913, P914, P915)
Note on AB17: 1 = AI1 2 = AI2 3 = AI1 - AI2
Note on C18: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on M18: 1 = Direct Acting (Forward Acting) 2 = Reverese Acting
Note on AB18: Expected PV when CO is 0 In eng units defined in P510, 511
Note on C19: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on AB19: Expected PV when CO is 100% In eng units defined in P510, 511
Note on AB20: If PV falls below this value for longer than the time in P925 - generate an alarm In units defined by P510, P511
Note on K21: 0 = Speed Ref. 4 = PTC 7 = PLC User app 16 = SP 17 = PV
Note on AB21: How long condition should remain before alarming. In seconds
Note on AB22: If PV goes above this value for longer than the time in P927 - generate an alarm In units defined by P510, P511
Note on K23: 0 = 0 to 10V OR 0-20mA 1 = 4 to 20 mA 2 = 10 to 0V OR 20 to 0mA 3 = 20 to 4mA
Note on AB23: How long condition should remain before alarming. In seconds
Note on AB24: 0 = disable PID controller 1 = Forward (or Direct) mode 2 = Reverse Mode
Note on AB25: 0 = Manual 1 = Automatic 2 = via DI2 M(0), A(1)
Note on AB26: Man->Auto Auto->Man 0 SP=SP SP=SP 1 SP=PV SP=SP (bumplees) 2 SP=SP SP=PV 3 SP=PV SP=PV (Bumpless)
Note on K27: Expected PV at CO = 0%
Note on C28: 0 = Always Local 1 = Always Remote 4 = Dix 5 = Seiral/USB LOCAL 6 = Serial/USB REMOTE 11 = SoftPLC
Note on K28: Expected PV at CO = 100%
Note on C29: 0 = HMI 1 = AI1 2 = AI2 3 = Potentiometer 4 = FI 5 = AI1+AI@ >0 6 = AI1 + AI2 7 = Elect Pot 8 = MultiSpeed 9 = Seia USB 12 = SoftPLC 14 AI1>0 15 = AI2 >0 16 = Potentiometer >0 17 = FI >0
Note on C30: 0 = HMI Keys 1 = Dix 2 = Serial USB 5 = SoftPLC
Note on C31: 0 = not used 1 = Run Stop … lots more ...
Note on I31: Units to show on LCD For Soft PLC Params 2 = V 3 = Hz 5 = % 7 = rpm all others show nothing
Note on C32: 0 = not used 1 = Run Stop … lots more .. 50 = PID Man/Auto
Note on I32: Decimal Point for Soft PLC Params 0 = wxyz 1 = wxy.z 2 = wx.yz 3 = w.xyz
Note on P32: (for 100% make it same as P208)
Note on I40: 0 = Speed Ref. 4 = PTC 7 = PLC User app 16 = SP 17 = PV
Note on O45: Folea, Rick: Scale the display for the speed reference in paramter 2. We'll enter that as a 600 for 60 Hz (and adjust the formatting parameters accordingly (P209, 210)
Note on O46: Decimal Point 0 = wxyz 1 = wxy.z 2 = wx.yz 3 = w.xyz
Note on O47: 2 = V 3 = Hz 5 = % 7 = rpm all others show nothing